## Sheet1
database | vanadium-redox-flow-battery
Activity | nafion membrane production
location | RER
production amount | 1
comment | The Vanadium Redox Flow Battery (VRFB) system is divided into two subsystems - a power and an energy sub-system - in accordance with the cell area related to the power and the electrolyte volume related to the energy storage capacity. Remaining components are assigned to the periphery. The considered VRFB system shows a rated power of 1 MW and an energy capacity of 8.3 MWh. The principal battery layout is derived from published literature, majorly a recent publication on stationary VRFB (Minke, C. Techno-ökonomische Modellierung Und Bewertung von Stationären, Vanadium-Redox-Flow-Batterien Im Industriellen Maßstab, 40th ed.; Cuvillier Verlag: Göttingen, 2016). The dimensions of the different parts provided there allow for calculating the battery composition on a mass basis. An 8.3 MWh system requires an electrolyte volume of 194 m3 and, assuming a void volume of 50%, a tank capacity of 300 m3. For a nominal power of 1 MW, two stacks with a total of 155 cells are required. Each stack is composed of a 105 membrane, a bipolar plates, two carbon felt electrodes, two current collector and the two associated gaskets.
source | Life Cycle Assessment of a Vanadium Redox Flow Battery, Selina Weber, Jens F. Peters, Manuel Baumann, and Marcel Weil, Environ. Sci. Technol. 2018, 52, 10864−10873, DOI: 10.1021/acs.est.8b02073
reference product | nafion membrane
type | process
unit | kilogram
Exchanges
name | amount | location | unit | categories | type | reference product | comment
nafion membrane production | 1 | RER | kilogram |  | production | nafion membrane
market for tetrafluoroethylene | 1 | GLO | kilogram |  | technosphere | tetrafluoroethylene | Tetrafluoroethylene (C2F4)
market for sulfur trioxide | 0.5 | RER | kilogram |  | technosphere | sulfur trioxide | Sulfur trioxide (SO3)
market for hexafluoroethane | 3.2 | GLO | kilogram |  | technosphere | hexafluoroethane | Hexafluoropropene (C3F6)
market for sodium hypochlorite, without water, in 15% solution state | 3 | RER | kilogram |  | technosphere | sodium hypochlorite, without water, in 15% solution state | Sodium hypochlorite (NaOCl)
market for sodium hydroxide, without water, in 50% solution state | 0.6 | GLO | kilogram |  | technosphere | sodium hydroxide, without water, in 50% solution state | Sodium hydroxide (NaOH)
market for soda ash, dense | 0.11 | GLO | kilogram |  | technosphere | soda ash, dense | Sodium carbonate (Na2CO3)
chemical factory construction, organics | 4e-10 | RER | unit |  | technosphere | chemical factory, organics | Infrastructure
market for heat, district or industrial, natural gas | 39.31 | Europe without Switzerland | megajoule |  | technosphere | heat, district or industrial, natural gas | Process heat
market for transport, freight, lorry, unspecified | 0.87 | RER | ton kilometer |  | technosphere | transport, freight, lorry, unspecified
market for transport, freight train | 5.22 | Europe without Switzerland | ton kilometer |  | technosphere | transport, freight train
Sodium chlorate | 2.36 |  | kilogram | water | biosphere |  | NaCl
Sodium hydroxide | 1.87 |  | kilogram | air | biosphere |  | NaOH, aqueous solution
Carbon dioxide, fossil | 0.0888 |  | kilogram | air | biosphere |  | CO2
treatment of spent solvent mixture, hazardous waste incineration, with energy recovery | -2.81 | Europe without Switzerland | kilogram |  | technosphere | spent solvent mixture | Organic residue
treatment of waste plastic, mixture, municipal incineration | -0.11 | CH | kilogram |  | technosphere | waste plastic, mixture | Plastic residue
treatment of bilge oil, hazardous waste incineration | -0.38 | Europe without Switzerland | kilogram |  | technosphere | bilge oil | Oily residue
Activity | polyacrylonitrile-based electrode production, for VRFB system
location | RER
production amount | 1
comment | The subsequent steps for the production of PAN-based carbon felt, oxidation and carbonization are modelled explicitly and therefore examined more closely since there are no suitable reference processes in ecoinvent. Mass balances are calculated according to stoichiometry. First, the thermal treatment (oxidation) and thus the stabilization of the felt is carried out. Under air oxidation, the PAN raw felt is treated at 300 °C for about one hour. The goal is to transform the felt into an infusible form by stretching and cyclizing the fibres. The heat input of the oxidation process is calculated by means of the heat capacity of polyacrylonitrile. The polyacrylonitrile is heated up from ambient temperature to 300 °C, requiring 0.87 MJ of energy. An efficiency of 85 % of the furnace is assumed. In the following processing step, carbonization is carried out in an inert nitrogen atmosphere at temperatures of up to 1500 °C.
source | Life Cycle Assessment of a Vanadium Redox Flow Battery, Selina Weber, Jens F. Peters, Manuel Baumann, and Marcel Weil, Environ. Sci. Technol. 2018, 52, 10864−10873, DOI: 10.1021/acs.est.8b02073
reference product | polyacrylonitrile-based electrode, for VFRB system
type | process
unit | kilogram
Exchanges
name | amount | location | unit | categories | type | reference product | comment
polyacrylonitrile-based electrode production, for VRFB system | 1 | RER | kilogram |  | production | polyacrylonitrile-based electrode, for VFRB system
carbon fiber production, weaved, at factory | 2 | RER | kilogram |  | technosphere | carbon fiber, weaved | Raw carbon felt
market for heat, district or industrial, natural gas | 0.87 | Europe without Switzerland | megajoule |  | technosphere | heat, district or industrial, natural gas | Heat, Oxidation
market for heat, district or industrial, natural gas | 5.25 | Europe without Switzerland | megajoule |  | technosphere | heat, district or industrial, natural gas | Heat, Carbonization
market for natural gas, burned in gas turbine | 0.0796 | GLO | megajoule |  | technosphere | natural gas, burned in gas turbine | Fuel demand, RTO
Carbon dioxide, fossil | 1.31 |  | kilogram | air | biosphere |  | CO2
Nitrogen | 0.67 |  | kilogram | air | biosphere |  | N2
Water | 0.00066 |  | cubic meter | air | biosphere |  | H2O
Activity | biopolar plate production, for VRFB system
location | RER
production amount | 1
comment | The materials of the bipolar plate must have particular properties because of its multiple responsibilities and the challenging environment in which the VRFB operates. This study focuses on a compound material consisting of synthetic graphite and polypropylene as a binder since these compound components are particularly suitable for redox flow batteries. The mass balance is based on a data sheet from a manufacturer of bipolar plates.
source | Life Cycle Assessment of a Vanadium Redox Flow Battery, Selina Weber, Jens F. Peters, Manuel Baumann, and Marcel Weil, Environ. Sci. Technol. 2018, 52, 10864−10873, DOI: 10.1021/acs.est.8b02073
reference product | biopolar plate, for VRFB system
type | process
unit | kilogram
Exchanges
name | amount | location | unit | categories | type | reference product | comment
biopolar plate production, for VRFB system | 1 | RER | kilogram |  | production | biopolar plate, for VRFB system
market for graphite, battery grade | 0.88 | GLO | kilogram |  | technosphere | graphite, battery grade | Synthetic graphite
market for polypropylene, granulate | 0.14 | GLO | kilogram |  | technosphere | polypropylene, granulate | Polypropylene
market for lubricating oil | 0.00022 | RER | kilogram |  | technosphere | lubricating oil | Oil
market for packaging box factory | 2.8e-09 | GLO | unit |  | technosphere | packaging box factory | Infrastructure
market for laminated timber element, transversally prestressed, for outdoor use | 4.3e-05 | RER | cubic meter |  | technosphere | laminated timber element, transversally prestressed, for outdoor use | Particle board
market for core board | 0.0146 | GLO | kilogram |  | technosphere | core board | Core board
market for EUR-flat pallet | 0.00288 | RER | unit |  | technosphere | EUR-flat pallet | Pallet
market for solid bleached and unbleached board carton | 0.00196 | RER | kilogram |  | technosphere | solid bleached and unbleached board carton | Bleached board
market for water, deionised | 0.0874 | Europe without Switzerland | kilogram |  | technosphere | water, deionised | Water
market for steam, in chemical industry | 0.12 | RER | kilogram |  | technosphere | steam, in chemical industry | Steam
market for heat, district or industrial, natural gas | 0.42 | Europe without Switzerland | megajoule |  | technosphere | heat, district or industrial, natural gas | Heat
market for heat, district or industrial, natural gas | 1.2 | Europe without Switzerland | megajoule |  | technosphere | heat, district or industrial, natural gas | Heat
market group for electricity, medium voltage | 1.32 | RER | kilowatt hour |  | technosphere | electricity, medium voltage | Electricity
market for transport, freight, lorry 16-32 metric ton, EURO5 | 0.1 | RER | ton kilometer |  | technosphere | transport, freight, lorry 16-32 metric ton, EURO5 | Transport, lorry
market for transport, freight train | 0.21 | Europe without Switzerland | ton kilometer |  | technosphere | transport, freight train | Transport, train
treatment of waste plastic, mixture, municipal incineration | -0.025 | CH | kilogram |  | technosphere | waste plastic, mixture | Plastic residue
Activity | stack frame assembly, for VRFB system
location | RER
production amount | 1
comment | The stack frame is a steel structure consisting of two double T-profiles which correspond to the dimensions of the stack. The dimension and weight are estimated based on a technical datasheet for a representative steel profile.
source | Life Cycle Assessment of a Vanadium Redox Flow Battery, Selina Weber, Jens F. Peters, Manuel Baumann, and Marcel Weil, Environ. Sci. Technol. 2018, 52, 10864−10873, DOI: 10.1021/acs.est.8b02073
reference product | stack frame, for VRFB system
type | process
unit | kilogram
Exchanges
name | amount | location | unit | categories | type | reference product | comment
stack frame assembly, for VRFB system | 1 | RER | kilogram |  | production | stack frame, for VRFB system
market for steel, low-alloyed | 1 | GLO | kilogram |  | technosphere | steel, low-alloyed | Steel frame, material
market for metal working, average for steel product manufacturing | 1 | GLO | kilogram |  | technosphere | metal working, average for steel product manufacturing | Steel frame, processing
market for welding, arc, steel | 0.0326 | GLO | meter |  | technosphere | welding, arc, steel | T-Profile welding
market for transport, freight, lorry 16-32 metric ton, EURO5 | 0.1 | RER | ton kilometer |  | technosphere | transport, freight, lorry 16-32 metric ton, EURO5 | Transport, lorry, steel
market for transport, freight train | 0.2 | Europe without Switzerland | ton kilometer |  | technosphere | transport, freight train | Transport, train, steel
Activity | vanadium electrolyte solution production
location | RER
production amount | 1
comment | The electrolyte composition is derived from technical data sheet of the manufacturer Gfe GmbH, and is confirmed by private correspondence with experts. The vanadium concentration within the electrolyte is 1.6 mol / L and the sulfate concentration 2 mol / L. Additionally, 0.05 mol / L of phosphoric acid is used as a stabilizer. The mass fractions of the four components vanadium, sulfuric acid, phosphoric acid and water are calculated taking into account the molar mass as well as the density of the electrolyte. The density of the electrolyte consequently corresponds to 1.35 kg / L.
source | Life Cycle Assessment of a Vanadium Redox Flow Battery, Selina Weber, Jens F. Peters, Manuel Baumann, and Marcel Weil, Environ. Sci. Technol. 2018, 52, 10864−10873, DOI: 10.1021/acs.est.8b02073
reference product | vanadium electrolyte solution
type | process
unit | kilogram
Exchanges
name | amount | location | unit | categories | type | reference product | comment
vanadium electrolyte solution production | 1 | RER | kilogram |  | production | vanadium electrolyte solution
vanadium pentoxide production | 0.286 | ZA | kilogram |  | technosphere | vanadium pentoxide | Vanadium pentoxide
market for sulfuric acid | 0.196 | RER | kilogram |  | technosphere | sulfuric acid | Sulfuric acid
market for phosphoric acid, industrial grade, without water, in 85% solution state | 0.004899 | GLO | kilogram |  | technosphere | phosphoric acid, industrial grade, without water, in 85% solution state | Phosphoric acid
market for water, deionised | 0.863 | Europe without Switzerland | kilogram |  | technosphere | water, deionised | Water
market for transport, freight, lorry 16-32 metric ton, EURO5 | 0.02 | RER | ton kilometer |  | technosphere | transport, freight, lorry 16-32 metric ton, EURO5 | Transport, lorry
market for transport, freight train | 0.121 | Europe without Switzerland | ton kilometer |  | technosphere | transport, freight train | Transport, train
market for transport, freight, sea, container ship | 3.813 | GLO | ton kilometer |  | technosphere | transport, freight, sea, container ship | Transport, ship overseas
market for transport, freight, inland waterways, barge | 0.173 | RER | ton kilometer |  | technosphere | transport, freight, inland waterways, barge | Transport, barge
market for transport, freight, lorry, unspecified | 0.187 | RER | ton kilometer |  | technosphere | transport, freight, lorry, unspecified | Transport lorry (ZA)
Activity | electrolyte tank production, for VRFB system
location | RER
production amount | 1
comment | The vanadium electrolyte is stored in plastic tanks. These tanks must be composed of materials which are resistant to corrosion in the very low pH environment. Glass fiber with a PVC inline is selected as a particularly suitable material. It is assumed that each tank has a volume of 50 m3. According to the literature, the total tank volume for a VRFB configuration with a rated power of 1 MW and an energy capacity of 8.3 MWh is 300 m3. Therefore, six tanks for the stated total tank volume are required.
source | Life Cycle Assessment of a Vanadium Redox Flow Battery, Selina Weber, Jens F. Peters, Manuel Baumann, and Marcel Weil, Environ. Sci. Technol. 2018, 52, 10864−10873, DOI: 10.1021/acs.est.8b02073
reference product | electrolyte tank
type | process
unit | kilogram
Exchanges
name | amount | location | unit | categories | type | reference product | comment
electrolyte tank production, for VRFB system | 1 | RER | kilogram |  | production | electrolyte tank
market for polyester resin, unsaturated | 0.41 | RER | kilogram |  | technosphere | polyester resin, unsaturated
market for glass fibre | 0.62 | GLO | kilogram |  | technosphere | glass fibre
market for chemical, organic | 0.0245 | GLO | kilogram |  | technosphere | chemical, organic
market for polyvinylchloride, emulsion polymerised | 0.0219 | GLO | kilogram |  | technosphere | polyvinylchloride, emulsion polymerised
market for extrusion, plastic pipes | 0.0219 | GLO | kilogram |  | technosphere | extrusion, plastic pipes
market for transport, freight train | 0.21 | Europe without Switzerland | ton kilometer |  | technosphere | transport, freight train | Transport, train
market for transport, freight, lorry 16-32 metric ton, EURO5 | 0.11 | RER | ton kilometer |  | technosphere | transport, freight, lorry 16-32 metric ton, EURO5
market for transport, freight, sea, container ship | 1.06 | GLO | ton kilometer |  | technosphere | transport, freight, sea, container ship
treatment of waste mineral wool, collection for final disposal | -0.0514 | Europe without Switzerland | kilogram |  | technosphere | waste mineral wool
Hydrocarbons, aromatic | 6.25e-05 |  | kilogram | air | biosphere
Activity | current collector production, for VRFB system
location | RER
production amount | 1
comment | As a current collector, copper plates with a thickness of 20 mm are used at both ends of the stack. It is assumed that 1 kg of copper is required for the production of 1 kg of current collector. The processing of the plate is assumed to be sheet rolled. Accordingly, the ecoinvent dataset “sheet rolling, copper” is applied.
source | Life Cycle Assessment of a Vanadium Redox Flow Battery, Selina Weber, Jens F. Peters, Manuel Baumann, and Marcel Weil, Environ. Sci. Technol. 2018, 52, 10864−10873, DOI: 10.1021/acs.est.8b02073
reference product | current collector, for VRFB system
type | process
unit | kilogram
Exchanges
name | amount | location | unit | categories | type | reference product | comment
current collector production, for VRFB system | 1 | RER | kilogram |  | production | current collector, for VRFB system
market for copper, cathode | 1 | GLO | kilogram |  | technosphere | copper, cathode | Copper plate, material
market for sheet rolling, copper | 1 | GLO | kilogram |  | technosphere | sheet rolling, copper | Copper plate, processing
market for metal working factory | 4e-10 | GLO | unit |  | technosphere | metal working factory | Infrastructure
market for transport, freight, lorry 16-32 metric ton, EURO5 | 0.1 | RER | ton kilometer |  | technosphere | transport, freight, lorry 16-32 metric ton, EURO5 | Transport, lorry
market for transport, freight train | 0.2 | Europe without Switzerland | ton kilometer |  | technosphere | transport, freight train | Transport, train
Activity | polyvinylchloride cell frame production, for VRFB system
location | RER
production amount | 1
comment | Each cell is surrounded by an extruded polyvinylchloride (PVC) frame. Thus, the corresponding ecoinvent dataset for polyvinylchloride is used. Since the frame is shaped by extrusion, the corresponding ecoinvent dataset is applied.
source | Life Cycle Assessment of a Vanadium Redox Flow Battery, Selina Weber, Jens F. Peters, Manuel Baumann, and Marcel Weil, Environ. Sci. Technol. 2018, 52, 10864−10873, DOI: 10.1021/acs.est.8b02073
reference product | polyvinylchloride cell frame, for VRFB system
type | process
unit | kilogram
Exchanges
name | amount | location | unit | categories | type | reference product | comment
polyvinylchloride cell frame production, for VRFB system | 1 | RER | kilogram |  | production | polyvinylchloride cell frame, for VRFB system
market for polyvinylchloride, emulsion polymerised | 1 | GLO | kilogram |  | technosphere | polyvinylchloride, emulsion polymerised | Polyvinylchloride
market for extrusion, plastic pipes | 1 | GLO | kilogram |  | technosphere | extrusion, plastic pipes | Extrusion
market for transport, freight train | 0.2 | Europe without Switzerland | ton kilometer |  | technosphere | transport, freight train | Transport, train
market for transport, freight, lorry 16-32 metric ton, EURO5 | 0.1 | RER | ton kilometer |  | technosphere | transport, freight, lorry 16-32 metric ton, EURO5 | Transport, lorry
Activity | gasket production, FKM, for VRFB system
location | RER
production amount | 1
comment | FKM gaskets represent the first modeled variant. An important type of FKM is the terpolymer consisting of vinylidene fluoride (VDF), hexafluoropropylene (HFP) and tetrafluoroethylene (TFE). The respective ecoinvent datasets of the chemicals are used in which HFE is approximated by HFP and VFD by polyvinyl fluoride. As a forming process, the reference process “extrusion, plastic pipes” is used.
source | Life Cycle Assessment of a Vanadium Redox Flow Battery, Selina Weber, Jens F. Peters, Manuel Baumann, and Marcel Weil, Environ. Sci. Technol. 2018, 52, 10864−10873, DOI: 10.1021/acs.est.8b02073
reference product | gasket, FKM
type | process
unit | kilogram
Exchanges
name | amount | location | unit | categories | type | reference product | comment
gasket production, FKM, for VRFB system | 1 | RER | kilogram |  | production | gasket, FKM
market for hexafluoroethane | 0.33 | GLO | kilogram |  | technosphere | hexafluoroethane | HFE
market for tetrafluoroethylene | 0.33 | GLO | kilogram |  | technosphere | tetrafluoroethylene | TFE
market for polyvinylfluoride | 0.33 | GLO | kilogram |  | technosphere | polyvinylfluoride | Polyvinyl fluoride
market for extrusion, plastic pipes | 1 | GLO | kilogram |  | technosphere | extrusion, plastic pipes | Extrusion, plastic pipes
market for transport, freight train | 0.2 | Europe without Switzerland | ton kilometer |  | technosphere | transport, freight train | Transport, rail
market for transport, freight, lorry 16-32 metric ton, EURO5 | 0.1 | RER | ton kilometer |  | technosphere | transport, freight, lorry 16-32 metric ton, EURO5 | Transport, lorry
Activity | copper cable production, for VRFB system
location | RER
production amount | 1
comment | FKM gaskets represent the first modeled variant. An important type of FKM is the terpolymer consisting of vinylidene fluoride (VDF), hexafluoropropylene (HFP) and tetrafluoroethylene (TFE). The respective ecoinvent datasets of the chemicals are used in which HFE is approximated by HFP and VFD by polyvinyl fluoride. As a forming process, the reference process “extrusion, plastic pipes” is used.
source | Life Cycle Assessment of a Vanadium Redox Flow Battery, Selina Weber, Jens F. Peters, Manuel Baumann, and Marcel Weil, Environ. Sci. Technol. 2018, 52, 10864−10873, DOI: 10.1021/acs.est.8b02073
reference product | copper cable, for VRFB system
type | process
unit | kilogram
Exchanges
name | amount | location | unit | categories | type | reference product | comment
copper cable production, for VRFB system | 1 | RER | kilogram |  | production | copper cable, for VRFB system
market for tap water | 1.45 | Europe without Switzerland | kilogram |  | technosphere | tap water | Tap water
market for copper, cathode | 0.94 | GLO | kilogram |  | technosphere | copper, cathode | Copper
market for polyvinylchloride, emulsion polymerised | 0.0626 | GLO | kilogram |  | technosphere | polyvinylchloride, emulsion polymerised | PVC
market for wire drawing, copper | 0.94 | GLO | kilogram |  | technosphere | wire drawing, copper | Wire drawing
market for extrusion, plastic pipes | 0.0626 | GLO | kilogram |  | technosphere | extrusion, plastic pipes | Extrusion
market for rolling mill | 1.77e-12 | GLO | unit |  | technosphere | rolling mill | Infrastructure
market for transport, freight, lorry 16-32 metric ton, EURO5 | 0.0937 | RER | ton kilometer |  | technosphere | transport, freight, lorry 16-32 metric ton, EURO5 | Transport, lorry
market for transport, freight train | 0.19 | Europe without Switzerland | ton kilometer |  | technosphere | transport, freight train | Transport, train
treatment of hazardous waste, hazardous waste incineration | -0.000317 | Europe without Switzerland | kilogram |  | technosphere | hazardous waste, for incineration | Disposal
treatment of waste plastic, mixture, municipal incineration | -0.000337 | CH | kilogram |  | technosphere | waste plastic, mixture | Disposal
Water | 8.86e-05 |  | cubic meter | air | biosphere |  | Water
Water | 0.00136 |  | cubic meter | water | biosphere |  | Water
Activity | pumps assembly, for VRFB system
location | RER
production amount | 1
comment | Two centrifugal pumps are required to pump the electrolyte into the cells. In addition, in each electrolyte circuit, two pumps are arranged redundantly. For the design of the pump it is assumed that the effective volume flow is 200 m3/h. The required size and mass of the pump can be derived from the data given in the technical data sheets from commercial providers of centrifugal pumps. Here, the flow rate is used as the basis for further calculations. As a result, the weight per pump is calculated to be 145 kg. Since there is no further information on the exact composition of the various materials for the production of the centrifugal pump, a reference process from ecoinvent is used for 408 assistance (pump production, 40 W). The required masses of the raw materials are adapted correspondingly, since the modeled VRFB pumps have a higher power.
source | Life Cycle Assessment of a Vanadium Redox Flow Battery, Selina Weber, Jens F. Peters, Manuel Baumann, and Marcel Weil, Environ. Sci. Technol. 2018, 52, 10864−10873, DOI: 10.1021/acs.est.8b02073
reference product | pumps, for VRFB system
type | process
unit | kilogram
Exchanges
name | amount | location | unit | categories | type | reference product | comment
pumps assembly, for VRFB system | 1 | RER | kilogram |  | production | pumps, for VRFB system
market for aluminium, wrought alloy | 0.00825 | GLO | kilogram |  | technosphere | aluminium, wrought alloy | Aluminum
market for cast iron | 0.49 | GLO | kilogram |  | technosphere | cast iron | Iron
market for copper, cathode | 0.1 | GLO | kilogram |  | technosphere | copper, cathode | Copper
market for polyvinylchloride, emulsion polymerised | 0.00158 | GLO | kilogram |  | technosphere | polyvinylchloride, emulsion polymerised | PVC
market for polyvinylchloride, suspension polymerised | 0.0108 | GLO | kilogram |  | technosphere | polyvinylchloride, suspension polymerised | PVC
market for steel, chromium steel 18/8, hot rolled | 0.38 | GLO | kilogram |  | technosphere | steel, chromium steel 18/8, hot rolled | Stainless steel
market for synthetic rubber | 0.00289 | GLO | kilogram |  | technosphere | synthetic rubber | Rubber
market for hot water tank factory | 2e-07 | GLO | unit |  | technosphere | hot water tank factory | Infrastructure
market for transport, freight, lorry 16-32 metric ton, EURO5 | 0.1 | RER | ton kilometer |  | technosphere | transport, freight, lorry 16-32 metric ton, EURO5 | Transport, lorry
market for transport, freight train | 0.2 | Europe without Switzerland | ton kilometer |  | technosphere | transport, freight train | Transport, train
treatment of waste plastic, mixture, municipal incineration | -0.00289 | CH | kilogram |  | technosphere | waste plastic, mixture | Disposal
market for waste polyvinylchloride product | -0.0124 | Europe without Switzerland | kilogram |  | technosphere | waste polyvinylchloride product | Disposal
Activity | pipes assembly, for VRFB system
location | RER
production amount | 1
comment | The pipes are steel pipes with a Teflon® lining. The required length of the cables is derived from the stack geometry so that a length of 30 meters is required for each electrolyte circuit. In addition, 5 meters of pipeline per stack are required. It is assumed that a standard pipe with the diameter DN 418 50 (60.3 mm) is used and that the Teflon® lining is 1 mm. By means of the density and the 419 dimensions, the required quantity of steel and Teflon® can be calculated. Since there is no ecoinvent dataset for Teflon®, TFE is used as approximation. The ecoinvent standard distances are applied for steel and plastics respectively.
source | Life Cycle Assessment of a Vanadium Redox Flow Battery, Selina Weber, Jens F. Peters, Manuel Baumann, and Marcel Weil, Environ. Sci. Technol. 2018, 52, 10864−10873, DOI: 10.1021/acs.est.8b02073
reference product | pipes, for VRFB system
type | process
unit | kilogram
Exchanges
name | amount | location | unit | categories | type | reference product | comment
pipes assembly, for VRFB system | 1 | RER | kilogram |  | production | pipes, for VRFB system
market for steel, chromium steel 18/8 | 0.87 | GLO | kilogram |  | technosphere | steel, chromium steel 18/8 | Steel, material
market for tetrafluoroethylene film, on glass | 0.13 | GLO | kilogram |  | technosphere | tetrafluoroethylene film, on glass | Teflon® lining
market for drawing of pipe, steel | 0.87 | GLO | kilogram |  | technosphere | drawing of pipe, steel | Processing, steel
market for transport, freight, lorry 16-32 metric ton, EURO5 | 0.1 | RER | ton kilometer |  | technosphere | transport, freight, lorry 16-32 metric ton, EURO5 | Transport, lorry
market for transport, freight train | 0.2 | Europe without Switzerland | ton kilometer |  | technosphere | transport, freight train | Transport, train
Activity | heat exchanger production, for VRFB system
location | RER
production amount | 1
comment | The heat exchanger used is a plate heat exchanger whose design is based on the heat exchange surface and the needed capacity of 1 MW. Since there is no information available regarding the heat exchanger, data from a heat exchanger from a secondary publication are used and scaled accordingly. The technical design of the heat exchanger for the VRFB is based on C. Minke. The required quantities of raw materials, as well as the energy and heat demand, are adjusted by means of the heat flow. It is assumed that the whole heat exchanger is made of stainless steel since other materials account for a very small mass32. Furthermore, the production of the heat exchanger is assumed to take place in Sweden and thus, transport distances from Sweden to Germany are applied.
source | Life Cycle Assessment of a Vanadium Redox Flow Battery, Selina Weber, Jens F. Peters, Manuel Baumann, and Marcel Weil, Environ. Sci. Technol. 2018, 52, 10864−10873, DOI: 10.1021/acs.est.8b02073
reference product | heat exchanger, for VRFB system
type | process
unit | kilogram
Exchanges
name | amount | location | unit | categories | type | reference product | comment
heat exchanger production, for VRFB system | 1 | RER | kilogram |  | production | heat exchanger, for VRFB system
market for steel, chromium steel 18/8 | 1 | GLO | kilogram |  | technosphere | steel, chromium steel 18/8 | Stainless steel
market for hot rolling, steel | 1 | GLO | kilogram |  | technosphere | hot rolling, steel | Processing, stainless steel
market group for electricity, medium voltage | 0.075 | RER | kilowatt hour |  | technosphere | electricity, medium voltage | Electricity
market for heat, district or industrial, natural gas | 0.54 | Europe without Switzerland | megajoule |  | technosphere | heat, district or industrial, natural gas | Heat
market for transport, freight, lorry 16-32 metric ton, EURO5 | 0.05 | RER | ton kilometer |  | technosphere | transport, freight, lorry 16-32 metric ton, EURO5 | Transport, lorry
market for transport, freight train | 1.16 | Europe without Switzerland | ton kilometer |  | technosphere | transport, freight train | Transport, train
Activity | stack monitoring interface assembly, for VRFB system
location | RER
production amount | 1
comment | Here, it is assumed that a monitoring system is required per stack and thus one BMS is required to control them. It must be noted that this is assumed to be major simplification, while the process control system is a relevant component. In fact, the modeling of the process control system is a crucial aspect since electronics potentially show high impacts in several categories. Therefore, this major gap needs to be fulfilled by future research.
source | Life Cycle Assessment of a Vanadium Redox Flow Battery, Selina Weber, Jens F. Peters, Manuel Baumann, and Marcel Weil, Environ. Sci. Technol. 2018, 52, 10864−10873, DOI: 10.1021/acs.est.8b02073
reference product | stack monitoring interface, for VRFB system
type | process
unit | kilogram
Exchanges
name | amount | location | unit | categories | type | reference product | comment
stack monitoring interface assembly, for VRFB system | 1 | RER | kilogram |  | production | stack monitoring interface, for VRFB system
market for steel, low-alloyed | 0.77 | GLO | kilogram |  | technosphere | steel, low-alloyed | Steel housing, material
market for electronics, for control units | 0.15 | GLO | kilogram |  | technosphere | electronics, for control units | Electronics, control
market for cable, unspecified | 0.0193 | GLO | kilogram |  | technosphere | cable, unspecified | Sensor cable
market for cable, data cable in infrastructure | 0.33 | GLO | meter |  | technosphere | cable, data cable in infrastructure | Data cable
market for polypropylene, granulate | 0.05 | GLO | kilogram |  | technosphere | polypropylene, granulate | Plastic parts and isolation
market for sheet rolling, steel | 0.77 | GLO | kilogram |  | technosphere | sheet rolling, steel | Processing, steel housing
market for injection moulding | 0.05 | GLO | kilogram |  | technosphere | injection moulding | Processing, plastic parts
market for transport, freight, lorry 16-32 metric ton, EURO5 | 0.1 | RER | ton kilometer |  | technosphere | transport, freight, lorry 16-32 metric ton, EURO5 | Transport, lorry
market for transport, freight train | 0.6 | Europe without Switzerland | ton kilometer |  | technosphere | transport, freight train | Transport, train
Activity | battery management system assembly, for VRFB system
location | RER
production amount | 1
comment | Here, it is assumed that a monitoring system is required per stack and thus one BMS is required to control them. It must be noted that this is assumed to be major simplification, while the process control system is a relevant component. In fact, the modeling of the process control system is a crucial aspect since electronics potentially show high impacts in several categories. Therefore, this major gap needs to be fulfilled by future research.
source | Life Cycle Assessment of a Vanadium Redox Flow Battery, Selina Weber, Jens F. Peters, Manuel Baumann, and Marcel Weil, Environ. Sci. Technol. 2018, 52, 10864−10873, DOI: 10.1021/acs.est.8b02073
reference product | battery management system, for VRFB system
type | process
unit | kilogram
Exchanges
name | amount | location | unit | categories | type | reference product | comment
battery management system assembly, for VRFB system | 1 | RER | kilogram |  | production | battery management system, for VRFB system
market for polypropylene, granulate | 0.18 | GLO | kilogram |  | technosphere | polypropylene, granulate | PP housing, material
market for injection moulding | 0.18 | GLO | kilogram |  | technosphere | injection moulding | PP housing, production
market for liquid crystal display, unmounted | 0.68 | GLO | kilogram |  | technosphere | liquid crystal display, unmounted | Display
market for electronics, for control units | 0.32 | GLO | kilogram |  | technosphere | electronics, for control units | Electronics
market for transport, freight, lorry 16-32 metric ton, EURO5 | 0.1 | RER | ton kilometer |  | technosphere | transport, freight, lorry 16-32 metric ton, EURO5 | Transport, lorry
market for transport, freight train | 0.6 | Europe without Switzerland | ton kilometer |  | technosphere | transport, freight train | Transport, train
Activity | process control system assembly, for VRFB system
location | RER
production amount | 1
comment | Here, it is assumed that a monitoring system is required per stack and thus one BMS is required to control them. It must be noted that this is assumed to be major simplification, while the process control system is a relevant component. In fact, the modeling of the process control system is a crucial aspect since electronics potentially show high impacts in several categories. Therefore, this major gap needs to be fulfilled by future research.
source | Life Cycle Assessment of a Vanadium Redox Flow Battery, Selina Weber, Jens F. Peters, Manuel Baumann, and Marcel Weil, Environ. Sci. Technol. 2018, 52, 10864−10873, DOI: 10.1021/acs.est.8b02073
reference product | process control system, for VRFB system
type | process
unit | kilogram
Exchanges
name | amount | location | unit | categories | type | reference product | comment
process control system assembly, for VRFB system | 1 | RER | kilogram |  | production | process control system, for VRFB system
stack monitoring interface assembly, for VRFB system | 0.91 | RER | kilogram |  | technosphere | stack monitoring interface, for VRFB system | Monitoring
battery management system assembly, for VRFB system | 0.09 | RER | kilogram |  | technosphere | battery management system, for VRFB system | Battery management system
Activity | treatment of stack, for VRFB system
location | RER
production amount | 1
source | Life Cycle Assessment of a Vanadium Redox Flow Battery, Selina Weber, Jens F. Peters, Manuel Baumann, and Marcel Weil, Environ. Sci. Technol. 2018, 52, 10864−10873, DOI: 10.1021/acs.est.8b02073
reference product | used stack, for VRFB system
type | process
unit | kilogram
Exchanges
name | amount | location | unit | categories | type | reference product | comment
treatment of stack, for VRFB system | -1 | RER | kilogram |  | production | used stack, for VRFB system
market for waste polyvinylfluoride | -0.0838 | CH | kilogram |  | technosphere | waste polyvinylfluoride
market group for waste plastic, mixture | -0.56 | Europe without Switzerland | kilogram |  | technosphere | waste plastic, mixture
market for iron scrap, unsorted | -0.13 | GLO | kilogram |  | technosphere | iron scrap, unsorted
market for copper scrap, sorted, pressed | -0.2 | GLO | kilogram |  | technosphere | copper scrap, sorted, pressed
treatment of municipal solid waste, incineration | -0.0339 | CH | kilogram |  | technosphere | municipal solid waste
market group for electricity, low voltage | 0.01 | RER | kilowatt hour |  | technosphere | electricity, low voltage
market for diesel, burned in building machine | 0.1 | GLO | megajoule |  | technosphere | diesel, burned in building machine
Activity | treatment of electrolyte tank, for VRFB system
location | RER
production amount | 1
source | Life Cycle Assessment of a Vanadium Redox Flow Battery, Selina Weber, Jens F. Peters, Manuel Baumann, and Marcel Weil, Environ. Sci. Technol. 2018, 52, 10864−10873, DOI: 10.1021/acs.est.8b02073
reference product | used electrolyte tank, for VRFB system
type | process
unit | kilogram
Exchanges
name | amount | location | unit | categories | type | reference product | comment
treatment of electrolyte tank, for VRFB system | -1 | RER | kilogram |  | production | used electrolyte tank, for VRFB system
market group for electricity, low voltage | 0.01 | RER | kilowatt hour |  | technosphere | electricity, low voltage
market for transport, freight, lorry 16-32 metric ton, EURO5 | 0.05 | RER | ton kilometer |  | technosphere | transport, freight, lorry 16-32 metric ton, EURO5 | Transport, lorry
market group for waste plastic, mixture | -1 | Europe without Switzerland | kilogram |  | technosphere | waste plastic, mixture
Activity | treatment of electrolyte solution, for VRFB system
location | RER
production amount | 1
source | Life Cycle Assessment of a Vanadium Redox Flow Battery, Selina Weber, Jens F. Peters, Manuel Baumann, and Marcel Weil, Environ. Sci. Technol. 2018, 52, 10864−10873, DOI: 10.1021/acs.est.8b02073
reference product | used electrolyte solution, for VRFB system
type | process
unit | kilogram
Exchanges
name | amount | location | unit | categories | type | reference product | comment
treatment of electrolyte solution, for VRFB system | -1 | RER | kilogram |  | production | used electrolyte solution, for VRFB system
market group for electricity, low voltage | 0.0445 | RER | kilowatt hour |  | technosphere | electricity, low voltage
market for transport, freight, lorry 16-32 metric ton, EURO5 | 0.6 | RER | ton kilometer |  | technosphere | transport, freight, lorry 16-32 metric ton, EURO5 | Transport, lorry
Activity | treatment of periphericals, for VRFB system
location | RER
production amount | 1
source | Life Cycle Assessment of a Vanadium Redox Flow Battery, Selina Weber, Jens F. Peters, Manuel Baumann, and Marcel Weil, Environ. Sci. Technol. 2018, 52, 10864−10873, DOI: 10.1021/acs.est.8b02073
reference product | used periphericals, for VRFB system
type | process
unit | kilogram
Exchanges
name | amount | location | unit | categories | type | reference product | comment
treatment of periphericals, for VRFB system | -1 | RER | kilogram |  | production | used periphericals, for VRFB system
market group for electricity, low voltage | 0.01 | RER | kilowatt hour |  | technosphere | electricity, low voltage
market for diesel, burned in building machine | 0.1 | GLO | megajoule |  | technosphere | diesel, burned in building machine
market for copper scrap, sorted, pressed | -0.011 | GLO | kilogram |  | technosphere | copper scrap, sorted, pressed
treatment of used cable | -0.033 | GLO | kilogram |  | technosphere | used cable
treatment of waste electric and electronic equipment, shredding | -0.59 | GLO | kilogram |  | technosphere | waste electric and electronic equipment
market group for waste plastic, mixture | -0.22 | Europe without Switzerland | kilogram |  | technosphere | waste plastic, mixture
Activity | vanadium-redox flow battery stack assembly
location | RER
comment | The power capacity for this application is 1MW and the net storage capacity 6 MWh. The net capacity considers the internal inefficiencies of the batteries and the min SoC, requiring a certain oversizing of the batteries. For providing net 6 MWh, a nominal capacity of 8.3 MWh is required for the VRFB with the assumed operation parameters. The assumed lifetime of the stack is 10 years. The lifetime of the system is 20 years or 8176 cycle-lifes (49,000 MWh).
production amount | 1
source | Life Cycle Assessment of a Vanadium Redox Flow Battery, Selina Weber, Jens F. Peters, Manuel Baumann, and Marcel Weil, Environ. Sci. Technol. 2018, 52, 10864−10873, DOI: 10.1021/acs.est.8b02073
reference product | vanadium-redox flow battery stack
type | process
unit | unit
Exchanges
name | amount | location | unit | categories | type | reference product | comment
vanadium-redox flow battery stack assembly | 1 | RER | unit |  | production | vanadium-redox flow battery stack
nafion membrane production | 150 | RER | kilogram |  | technosphere | nafion membrane | Membrane
polyacrylonitrile-based electrode production, for VRFB system | 419 | RER | kilogram |  | technosphere | polyacrylonitrile-based electrode, for VFRB system | Electrode
biopolar plate production, for VRFB system | 5490 | RER | kilogram |  | technosphere | biopolar plate, for VRFB system | Bipolar plate
current collector production, for VRFB system | 1970 | RER | kilogram |  | technosphere | current collector, for VRFB system | Current collector
polyvinylchloride cell frame production, for VRFB system | 306 | RER | kilogram |  | technosphere | polyvinylchloride cell frame, for VRFB system | Cell frame
gasket production, FKM, for VRFB system | 428 | RER | kilogram |  | technosphere | gasket, FKM | Gaskets
stack frame assembly, for VRFB system | 1253 | RER | kilogram |  | technosphere | stack frame, for VRFB system | Stack frame
Activity | vanadium-redox flow battery system assembly, 8.3 megawatt hour
location | RER
comment | The power capacity for this application is 1MW and the net storage capacity 6 MWh. The net capacity considers the internal inefficiencies of the batteries and the min SoC, requiring a certain oversizing of the batteries. For providing net 6 MWh, a nominal capacity of 8.3 MWh is required for the VRFB with the assumed operation parameters. The assumed lifetime of the stack is 10 years. The lifetime of the system is 20 years or 8176 cycle-lifes (49,000 MWh).
production amount | 1
source | Life Cycle Assessment of a Vanadium Redox Flow Battery, Selina Weber, Jens F. Peters, Manuel Baumann, and Marcel Weil, Environ. Sci. Technol. 2018, 52, 10864−10873, DOI: 10.1021/acs.est.8b02073
reference product | vanadium-redox flow battery system
type | process
unit | unit
Exchanges
name | amount | location | unit | categories | type | reference product | comment
vanadium-redox flow battery system assembly, 8.3 megawatt hour | 1 | RER | unit |  | production | vanadium-redox flow battery system
vanadium-redox flow battery stack assembly | 1 | RER | unit |  | technosphere | vanadium-redox flow battery stack | Stack
vanadium electrolyte solution production | 272220 | RER | kilogram |  | technosphere | vanadium electrolyte solution | Electrolyte
electrolyte tank production, for VRFB system | 32589 | RER | kilogram |  | technosphere | electrolyte tank | Tank
pumps assembly, for VRFB system | 580 | RER | kilogram |  | technosphere | pumps, for VRFB system | Pumps
pipes assembly, for VRFB system | 332 | RER | kilogram |  | technosphere | pipes, for VRFB system | Pipes
market for inverter, 500kW | 2 | GLO | unit |  | technosphere | inverter, 500kW | Inverter
copper cable production, for VRFB system | 177 | RER | kilogram |  | technosphere | copper cable, for VRFB system | Cables
process control system assembly, for VRFB system | 13 | RER | kilogram |  | technosphere | process control system, for VRFB system | PCS
heat exchanger production, for VRFB system | 1023 | RER | kilogram |  | technosphere | heat exchanger, for VRFB system | Heat exchanger
Activity | electricity supply, high voltage, from vanadium-redox flow battery system
location | RER
comment | The power capacity for this application is 1MW and the net storage capacity 6 MWh. The net capacity considers the internal inefficiencies of the batteries and the min SoC, requiring a certain oversizing of the batteries. For providing net 6 MWh, a nominal capacity of 8.3 MWh is required for the VRFB with the assumed operation parameters. The assumed lifetime of the stack is 10 years. The lifetimeof the system is 20 years or 8176 cycle-lifes (49,000 MWh).
production amount | 1
source | Life Cycle Assessment of a Vanadium Redox Flow Battery, Selina Weber, Jens F. Peters, Manuel Baumann, and Marcel Weil, Environ. Sci. Technol. 2018, 52, 10864−10873, DOI: 10.1021/acs.est.8b02073
reference product | electricity, high voltage
type | process
unit | kilowatt hour
Exchanges
name | amount | location | unit | categories | type | reference product | comment
electricity supply, high voltage, from vanadium-redox flow battery system | 1 | RER | kilowatt hour |  | production | electricity, high voltage
market group for electricity, high voltage | 1.33 | RER | kilowatt hour |  | technosphere | electricity, high voltage | Electricity input plus losses
vanadium-redox flow battery system assembly, 8.3 megawatt hour | 2.0408e-08 | RER | unit |  | technosphere | vanadium-redox flow battery system | Infrastructure requirements 1/49000 MWh
vanadium-redox flow battery stack assembly | 2.0408e-08 | RER | unit |  | technosphere | vanadium-redox flow battery stack | Replacement stack
treatment of stack, for VRFB system | -0.00041 | RER | kilogram |  | technosphere | used stack, for VRFB system | EoL of both stack
treatment of electrolyte tank, for VRFB system | -0.00066 | RER | kilogram |  | technosphere | used electrolyte tank, for VRFB system | Electrolyte tank EoL
treatment of electrolyte solution, for VRFB system | -0.00555 | RER | kilogram |  | technosphere | used electrolyte solution, for VRFB system | Electrolyte EoL
treatment of periphericals, for VRFB system | -0.0001 | RER | kilogram |  | technosphere | used periphericals, for VRFB system | Peripherals EoL